## (A)
General Information 一般資料 | [10 empty] | Appendix 1 P.1 of 5
Date of Inspection 視察日期:
Premises Address 處所地址:
Name of Licensed Plumber 持牌水喉匠姓名:
Plumber's Licence Number 水喉匠牌照號碼:
Serial Number of Form WWO46 表格WWO46編號: | [9 empty] | Inspection Checklist 視察清單 (Section A) (A部)
Inspection Type (please tick) 視察類別 (請剔): |  |  | □ Final Inspection 最終視察 |  | □ Interim Inspection 中期視察 |  | □ Re-inspection 重新視察 | Type of Plumbing Works 水管工程類別 : ( ) *
A | B | Penalty Point / Demerit Point 罰分 /記分 | Defects/irregularities found? (please tick) 發現不合規格/不妥當之處? (請剔) |  |  | Type (FW, FL, FS) ^ 類別 (食水、沖廁水、消防供水) | Defects/irregularities (Please specify the extent and details of defects/irregularities, if any) 不合規格/不妥當之處(如有，則請訂明不合規格/不妥當的程度和詳情) | Details of Inspected Location (refers code below, if applicable) 已視察位置的詳情(請參見下方的編號，如適用) | Details (e.g. Brand Name/Model No., if available) 詳情 (例如品牌名稱/型號，如有的話) | Photo Taken ( Y / N ) 夾附圖片 ( 有 / 沒有 ) | Remarks 備註
Type 類別 | Contravention of WWO / WWR or Non-compliance with WA's Requirements 違反《水務設施條例》/《水務設施規例》或 不符合水務監督的要求 |  | Yes 是 | No 否 | Not Applicable 不適用
(A) Piping (including all pipes and fittings, and connection pipe) 喉管 (包括所有喉管與裝置，以及接駁喉) | (1) Pipe size less than minimum permissible size 水管尺寸小於准許的尺寸 | P
| (2) Not bitumen painted or hessian / other suitable material wrapped 未塗上瀝青或纏上麻布 /其他適當物料 | P
| (3) A bend or curve made in any pipe that will diminish the waterway or alter the internal diameter of the pipe 水管上有屈曲或彎位，而令水道變窄或改變水管的內部直徑 | P
| (4) Used / covered up prior to inspection 在視察前已經使用/覆蓋 | P
| (5) Pipe/fittings made of material not allowed or not complied with the prescribed standard 水管/裝置所用的材料並不獲批准或不符合規定的標準 | P
| (6) Leaded solder used for jointing pipes and fittings@ 使用含鉛焊料接駁喉管與裝置@ | P
| (7) Not of the materials already accepted by the Water Authority (WA) in WWO 1149 並非在WWO1149表格內水務監督已接納的物料 | D
| (8) Connection pipes not of the sizes or at the position already accepted by the WA 接駁喉管並非水務監督已接納的尺寸或位置 | D
@ If this contravention of WWO/WWR item is found, the Licensing Authority will consider initiating the procedures to deliberate cancellation or suspension of the plumber's licence. | [6 empty] | Code for Inspected Location已視察位置的編號:
如發現違反《水務設施條例》/《水務設施規例》，發牌當局將考慮啟動相關程序，以取消或暫時吊銷持牌水喉匠的牌照。 | [6 empty] | (a) underground pipe and connection pipe 地下喉管及接駁喉 | (g) master meter position 總水錶位 |  | (m) communal riser pipe 公用豎管
Please insert ü at the appropriate box under the "Defects/irregularities found?" column. 請在「發現不合規格/不妥當之處?」欄下的適當空格內加 ü。 | [6 empty] | (b) concealed pipework above ground 地面以上的隱藏喉管 | (h) check meter position 檢測錶位 |  | (n) communal down-feed pipe 公用下給管
^ Fresh Water 食水 (FW), Flushing Water 沖廁水 (FL), Fire Service 消防供水 (FS) | [6 empty] | (c) roof tank 天台儲水箱 | (i) meter position 水錶位 |  | (o) feed tank for swimming pool 游泳池供水箱
* Please insert the code for the corresponding type of plumbing works: 請加入相應水管工程類別的編號: | [6 empty] | (d) intermediate tank 中間儲水箱 | (j) master meter room總水錶房/chamber井 |  | (p) irrigation supply points 灌溉供水點
(a) Building of Storey 樓層 >=4 | [6 empty] | (e) break pressure tank 減壓缸 | (k) meter cabinet水錶櫃/room房 (typical典型) |  | (q) cleansing supply points 清洗用水供水點
(b) Building of Storey樓層 <4 | [6 empty] | (f) break tank 斷流水箱 | (l) meter cabinet水錶櫃/room 房(non-typical, please specify非典型, 請註明) |  | (r) hydrant, hose reel, sprinkler, fountain 消防龍頭、消防喉轆、消防花灑、噴水池
(c) Village House 村屋 | [9 empty] | (s) other location其他位置 (please specify請註明)
(d) Separate Meter 安裝獨立水錶
(e) Construction Supply 地盤供水 | [6 empty] | ASN 申請書編號:
Photos should be taken on defects / irregularities 須為不合規格/不妥當之處拍照
[7 empty] | WSD Inspection Staff 水務署視察人員 | Licensed Plumber 持牌水喉匠 |  | Registered Professional Engineer 註冊專業工程師
[7 empty] | Signature 簽名： | Signature 簽名： |  | Signature 簽名：
[7 empty] | Name 姓名： | Name 姓名： |  | Name 姓名：
[7 empty] | Post 職位： | Plumber's Licence No. 水喉匠牌照號碼： |  | RPE No. 註冊號碼：
[7 empty] | Date 日期： | Date 日期： |  | Date 日期：

## (B)
General Information 一般資料 | [10 empty] | Appendix 1 P.2 of 5
Date of Inspection 視察日期:
Premises Address 處所地址:
Name of Licensed Plumber 持牌水喉匠姓名:
Plumber's Licence Number 水喉匠牌照號碼:
Serial Number of Form WWO46 表格WWO46編號: | [9 empty] | Inspection Checklist 視察清單 (Section B) (B部)
Inspection Type (please tick) 視察類別 (請剔): |  |  | □ Final Inspection 最終視察 |  | □ Interim Inspection 中期視察 |  | □ Re-inspection 重新視察 | Type of Plumbing Works 水管工程類別 : ( ) *
A | B | Penalty Point / Demerit Point 罰分 /記分 | Defects/irregularities found? (please tick) 發現不合規格/不妥當之處? (請剔) |  |  | Type (FW, FL, FS) ^ 類別 (食水、沖廁水、消防供水) | Defects/irregularities (Please specify the extent and details of defects/irregularities, if any) 不合規格/不妥當之處(如有，則請訂明不合規格/不妥當的程度和詳情) | Details of Inspected Location (refers code below, if applicable) 已視察位置的詳情(請參見下方的編號，如適用) | Details (e.g. Brand Name/Model No., if available) 詳情 (例如品牌名稱/型號，如有的話) | Photo Taken ( Y / N ) 夾附圖片 ( 有 / 沒有 ) | Remarks 備註
Type 類別 | Contravention of WWO / WWR or Non-compliance with WA's Requirements 違反《水務設施條例》/《水務設施規例》或 不符合水務監督的要求 |  | Yes 是 | No 否 | Not Applicable 不適用
(B) Meter Position / Check Meter Position 錶位/檢測錶位 | (1A) Meter position / check meter position not at suitable height above the floor level 錶位/檢測錶位非位於地面以上的適當高度 | D
| (1B) Meter installed in a landscape area with a clear working headroom less than 2m 安裝於園境地帶的水錶，其空間作業高度少於2米 | D
| (1C) Meters not arranged in groups and housed in meter rooms / boxes / cabinet / chamber 水錶並非集中排列及安放在水錶房/箱/櫃/井中 | D
| (2) Meter room / box not located at the hoarding recess area of the construction site 建築地盤的錶房/箱不設在圍板凹處 | D
| (3) No loose jumper stopcock at inlet side of the meter 水錶入水處缺少皮心掣 | D
| (4) Working clearance at check meter position not meeting the minimum requirement 檢測錶位的工作空間沒有達到最低要求 | D
| (5) No non-return valve provided on the delivery side of the meter 水錶出水口的一方缺少止回流閥 | D
| (6) No fullway gate valve provided before meter position 水錶前缺少全通閥 | D
| (7) Meter room/meter cabinet not satisfying the architectural requirements 水錶房/水錶櫃沒有達到建築要求 | D
@ If this contravention of WWO/WWR item is found, the Licensing Authority will consider initiating the procedures to deliberate cancellation or suspension of the plumber's licence. | [6 empty] | Code for Inspected Location已視察位置的編號:
如發現違反《水務設施條例》/《水務設施規例》，發牌當局將考慮啟動相關程序，以取消或暫時吊銷持牌水喉匠的牌照。 | [6 empty] | (a) underground pipe and connection pipe 地下喉管及接駁喉 | (g) master meter position 總水錶位 |  | (m) communal riser pipe 公用豎管
Please insert ü at the appropriate box under the "Defects/irregularities found?" column. 請在「發現不合規格/不妥當之處?」欄下的適當空格內加 ü。 | [6 empty] | (b) concealed pipework above ground 地面以上的隱藏喉管 | (h) check meter position 檢測錶位 |  | (n) communal down-feed pipe 公用下給管
^ Fresh Water 食水 (FW), Flushing Water 沖廁水 (FL), Fire Service 消防供水 (FS) | [6 empty] | (c) roof tank 天台儲水箱 | (i) meter position 水錶位 |  | (o) feed tank for swimming pool 游泳池供水箱
* Please insert the code for the corresponding type of plumbing works: 請加入相應水管工程類別的編號: | [6 empty] | (d) intermediate tank 中間儲水箱 | (j) master meter room總水錶房/chamber井 |  | (p) irrigation supply points 灌溉供水點
(a) Building of Storey 樓層 >=4 | [6 empty] | (e) break pressure tank 減壓缸 | (k) meter cabinet水錶櫃/room房 (typical典型) |  | (q) cleansing supply points 清洗用水供水點
(b) Building of Storey樓層 <4 | [6 empty] | (f) break tank 斷流水箱 | (l) meter cabinet水錶櫃/room 房(non-typical, please specify非典型, 請註明) |  | (r) hydrant, hose reel, sprinkler, fountain 消防龍頭、消防喉轆、消防花灑、噴水池
(c) Village House 村屋 | [9 empty] | (s) other location其他位置 (please specify請註明)
(d) Separate Meter 安裝獨立水錶
(e) Construction Supply 地盤供水 | [6 empty] | ASN 申請書編號:
Photos should be taken on defects / irregularities須為不合規格/不妥當之處拍照
[7 empty] | WSD Inspection Staff 水務署視察人員 | Licensed Plumber 持牌水喉匠 |  | Registered Professional Engineer 註冊專業工程師
[7 empty] | Signature 簽名： | Signature 簽名： |  | Signature 簽名：
[7 empty] | Name 姓名： | Name 姓名： |  | Name 姓名：
[7 empty] | Post 職位： | Plumber's Licence No. 水喉匠牌照號碼： |  | RPE No. 註冊號碼：
[7 empty] | Date 日期： | Date 日期： |  | Date 日期：

## (C)
General Information 一般資料 | [10 empty] | Appendix P.3 of 5
Date of Inspection 視察日期:
Premises Address 處所地址:
Name of Licensed Plumber 持牌水喉匠姓名:
Plumber's Licence Number 水喉匠牌照號碼:
Serial Number of Form WWO46 表格WWO46編號: | [9 empty] | Inspection Checklist 視察清單 (Section C) (C部)
Inspection Type (please tick) 視察類別 (請剔): |  |  | □ Final Inspection 最終視察 |  | □ Interim Inspection 中期視察 |  | □ Re-inspection 重新視察 | Type of Plumbing Works 水管工程類別 : ( ) *
A | B | Penalty Point / Demerit Point 罰分 /記分 | Defects/irregularities found? (please tick) 發現不合規格/不妥當之處? (請剔) |  |  | Type (FW, FL, FS) ^ 類別 (食水、沖廁水、消防供水) | Defects/irregularities (Please specify the extent and details of defects/irregularities, if any) 不合規格/不妥當之處(如有，則請訂明不合規格/不妥當的程度和詳情) | Details of Inspected Location (refers code below, if applicable) 已視察位置的詳情(請參見下方的編號，如適用) | Details (e.g. Brand Name/Model No., if available) 詳情 (例如品牌名稱/型號，如有的話) | Photo Taken ( Y / N ) 夾附圖片 ( 有 / 沒有 ) | Remarks 備註
Type 類別 | Contravention of WWO / WWR or Non-compliance with WA's Requirements 違反《水務設施條例》/《水務設施規例》或 不符合水務監督的要求 |  | Yes 是 | No 否 | Not Applicable 不適用
(C) Storage Tanks 儲水缸 | (1) Tanks made of material not allowed or not complied with the prescribed standard 水缸所用的材料並不獲批准或不符合規定的標準 | P
| (2) No control valve at inlet fed by gravity 在入水位缺少利用天然水壓供水的控制閥 | P
| (3) No automatic control switch for inlet of storage tank fed by pumped supply 儲水缸的入水位缺少利用泵壓供水的自動控制開關 | P
| (4) No control valve/drain-off pipe at outlet 出水位缺少控制閥/排水管 | P
| (5) Overflow pipe of fresh water tank not made of a corrosion-resisting material 食水水缸的溢流管所用的物料並非抗腐蝕物料 | P
| (6) Overflow pipe undersized 溢流管尺寸太小 | P
| (7) Invert of the inlet or the outlet of ball float valve less than 25mm above the top of the overflow pipe 入水管倒拱或浮球閥出水口離溢流管的頂部不足25毫米 | P
| (8) Overflow pipe connected to a drain or sewer or to the overflow pipe from another tank 溢流管接駁至排水渠或污水渠或另一個水缸的溢流管 | P
| (9) Fresh water tank connected for storage of water other than that supplied from the waterworks 食水水缸接駁並作儲存來自水務設施以外所供應的用水 | P
| (10) Water tank not easily accessible or safe access by ladder not provided 水缸不容易通往或未有提供梯子作安全通道 | P
| (11) Tank not provided with lockable covers 水缸缺少可上鎖的封蓋 | P
| (12) Storage capacity exceeds the maximum permitted capacity 儲水量超過最高准許儲水量 | P
| (13) No physical break between potable & non-potable tanks 可飲用及非飲用水缸中間沒有實際分隔 | P
| (14) Ball float valves or floats made of material not allowed or not complied with the prescribed standard 浮球閥或浮體所用的物料並不獲批准或不符合規定的標準 | P
| (15) Ball float valve/float operated valve improperly installed/provided 浮球閥/浮體操作閥安裝/安置不當 | P
| (16) Fresh water tank not provided with lockable double sealed covers 食水水缸缺少可上鎖的雙邊密封箱蓋 | D
@ If this contravention of WWO/WWR item is found, the Licensing Authority will consider initiating the procedures to deliberate cancellation or suspension of the plumber's licence. | [6 empty] | Code for Inspected Location已視察位置的編號:
如發現違反《水務設施條例》/《水務設施規例》，發牌當局將考慮啟動相關程序，以取消或暫時吊銷持牌水喉匠的牌照。 | [6 empty] | (a) underground pipe and connection pipe 地下喉管及接駁喉 | (g) master meter position 總水錶位 |  | (m) communal riser pipe 公用豎管
Please insert ü at the appropriate box under the "Defects/irregularities found?" column. 請在「發現不合規格/不妥當之處?」欄下的適當空格內加 ü。 | [6 empty] | (b) concealed pipework above ground 地面以上的隱藏喉管 | (h) check meter position 檢測錶位 |  | (n) communal down-feed pipe 公用下給管
^ Fresh Water 食水 (FW), Flushing Water 沖廁水 (FL), Fire Service 消防供水 (FS) | [6 empty] | (c) roof tank 天台儲水箱 | (i) meter position 水錶位 |  | (o) feed tank for swimming pool 游泳池供水箱
* Please insert the code for the corresponding type of plumbing works: 請加入相應水管工程類別的編號: | [6 empty] | (d) intermediate tank 中間儲水箱 | (j) master meter room總水錶房/chamber井 |  | (p) irrigation supply points 灌溉供水點
(a) Building of Storey 樓層 >=4 | [6 empty] | (e) break pressure tank 減壓缸 | (k) meter cabinet水錶櫃/room房 (typical典型) |  | (q) cleansing supply points 清洗用水供水點
(b) Building of Storey樓層 <4 | [6 empty] | (f) break tank 斷流水箱 | (l) meter cabinet水錶櫃/room 房(non-typical, please specify非典型, 請註明) |  | (r) hydrant, hose reel, sprinkler, fountain 消防龍頭、消防喉轆、消防花灑、噴水池
(c) Village House 村屋 | [9 empty] | (s) other location其他位置 (please specify請註明)
(d) Separate Meter 安裝獨立水錶
(e) Construction Supply 地盤供水 | [6 empty] | ASN 申請書編號:
Photos should be taken on defects / irregularities須為不合規格/不妥當之處拍照
[7 empty] | WSD Inspection Staff 水務署視察人員 | Licensed Plumber 持牌水喉匠 |  | Registered Professional Engineer 註冊專業工程師
[7 empty] | Signature 簽名： | Signature 簽名： |  | Signature 簽名：
[7 empty] | Name 姓名： | Name 姓名： |  | Name 姓名：
[7 empty] | Post 職位： | Plumber's Licence No. 水喉匠牌照號碼： |  | RPE No. 註冊號碼：
[7 empty] | Date 日期： | Date 日期： |  | Date 日期：

## (D)
General Information 一般資料 | [7 empty] | TICK THIS BOX IF NO ONLINE REPLUMBING 如非同位更換水喉，請剔此格 |  | □ |  | Appendix 1 P.4 of 5
Date of Inspection 視察日期:
Premises Address 處所地址:
Name of Licensed Plumber 持牌水喉匠姓名:
Plumber's Licence Number 水喉匠牌照號碼:
Serial Number of Form WWO46 表格WWO46編號: | [10 empty] | Inspection Checklist 視察清單 (Section D) (D部)
Inspection Type (please tick) 視察類別 (請剔): |  |  | □ Final Inspection 最終視察 |  | □ Interim Inspection 中期視察 |  | □ Re-inspection 重新視察 |  | Type of Plumbing Works 水管工程類別 : ( ) *
A | B | Penalty Point / Demerit Point 罰分 /記分 | Defects/irregularities found? (please tick) 發現不合規格/不妥當之處? (請剔) |  |  | Type (FW, FL, FS) ^ 類別 (食水、沖廁水、消防供水) | Defects/irregularities (Please specify the extent and details of defects/irregularities, if any) 不合規格/不妥當之處(如有，則請訂明不合規格/不妥當的程度和詳情) |  | Details of Inspected Location (refers code below, if applicable) 已視察位置的詳情(請參見下方的編號，如適用) | Details (e.g. Brand Name/Model No., if available) 詳情 (例如品牌名稱/型號，如有的話) | Photo Taken ( Y / N ) 夾附圖片 ( 有 / 沒有 ) | Remarks 備註
Type 類別 | Contravention of WWO / WWR or Non-compliance with WA's Requirements 違反《水務設施條例》/《水務設施規例》或 不符合水務監督的要求 |  | Yes 是 | No 否 | Not Applicable 不適用
(D) Online Re-plumbing 同位更換水喉 | (1A) No low initial leaching rate fittings installed 沒有安裝低溶濾率配件 | D
| (1B) Fittings installed have not been pretreated for online re-plumbing works 安裝於同位更換水喉工程的配件沒有經過預先處理 | D
| (2) No temporary water supply arrangement implemented on site (where applicable) 沒有在地盤實施臨時供水的安排(如適用) | D
| (3) No arrangement implemented on site to notify affected customers not to use tap water for drinking and cooking purposes (where applicable) 沒有在地盤實施安排以通知受影響用戶勿取用水龍頭水作飲用及煮食用途(如適用) | D
| (4) Online re-plumbing works were carried out but has not been specifically mentioned in plumbing proposal 已進行同位更換水喉工程，但沒有在水管工程計劃中明確提及 | D
| (5) Solder joints were adopted on site but has not been specifically mentioned in plumbing proposal /WWO 46 已在地盤採用軟焊接口, 但沒有在水管工程計劃/WWO46表格內明確提及 | D
@ If this contravention of WWO/WWR item is found, the Licensing Authority will consider initiating the procedures to deliberate cancellation or suspension of the plumber's licence. | [6 empty] | Code for Inspected Location已視察位置的編號:
如發現違反《水務設施條例》/《水務設施規例》，發牌當局將考慮啟動相關程序，以取消或暫時吊銷持牌水喉匠的牌照。 | [6 empty] | (a) underground pipe and connection pipe 地下喉管及接駁喉 |  | (g) master meter position 總水錶位 |  | (m) communal riser pipe 公用豎管
Please insert ü at the appropriate box under the "Defects/irregularities found?" column. 請在「發現不合規格/不妥當之處?」欄下的適當空格內加 ü。 | [6 empty] | (b) concealed pipework above ground 地面以上的隱藏喉管 |  | (h) check meter position 檢測錶位 |  | (n) communal down-feed pipe 公用下給管
^ Fresh Water 食水 (FW), Flushing Water 沖廁水 (FL), Fire Service 消防供水 (FS) | [6 empty] | (c) roof tank 天台儲水箱 |  | (i) meter position 水錶位 |  | (o) feed tank for swimming pool 游泳池供水箱
* Please insert the code for the corresponding type of plumbing works: 請加入相應水管工程類別的編號: | [6 empty] | (d) intermediate tank 中間儲水箱 |  | (j) master meter room總水錶房/chamber井 |  | (p) irrigation supply points 灌溉供水點
(a) Building of Storey 樓層 >=4 | [6 empty] | (e) break pressure tank 減壓缸 |  | (k) meter cabinet水錶櫃/room房 (typical典型) |  | (q) cleansing supply points 清洗用水供水點
(b) Building of Storey樓層 <4 | [6 empty] | (f) break tank 斷流水箱 |  | (l) meter cabinet水錶櫃/room 房(non-typical, please specify非典型, 請註明) |  | (r) hydrant, hose reel, sprinkler, fountain 消防龍頭、消防喉轆、消防花灑、噴水池
(c) Village House 村屋 | [10 empty] | (s) other location其他位置 (please specify請註明)
(d) Separate Meter 安裝獨立水錶
(e) Construction Supply 地盤供水 | [6 empty] | ASN 申請書編號:
Photos should be taken on defects / irregularities須為不合規格/不妥當之處拍照
[7 empty] | WSD Inspection Staff 水務署視察人員 |  | Licensed Plumber 持牌水喉匠 |  | Registered Professional Engineer 註冊專業工程師
[7 empty] | Signature 簽名： |  | Signature 簽名： |  | Signature 簽名：
[7 empty] | Name 姓名： |  | Name 姓名： |  | Name 姓名：
[7 empty] | Post 職位： |  | Plumber's Licence No. 水喉匠牌照號碼： |  | RPE No. 註冊號碼：
[7 empty] | Date 日期： |  | Date 日期： |  | Date 日期：

## (E)
General Information 一般資料 | [10 empty] | Appendix 1 P.5 of 5
Date of Inspection 視察日期:
Premises Address 處所地址:
Name of Licensed Plumber 持牌水喉匠姓名:
Plumber's Licence Number 水喉匠牌照號碼:
Serial Number of Form WWO46 表格WWO46編號: | [9 empty] | Inspection Checklist 視察清單 (Section E) (E部)
Inspection Type (please tick) 視察類別 (請剔): |  |  | □ Final Inspection 最終視察 |  | □ Interim Inspection 中期視察 |  | □ Re-inspection 重新視察 | Type of Plumbing Works 水管工程類別 : ( ) *
A | B | Penalty Point / Demerit Point 罰分/記分 | Defects/irregularities found? (please tick) 發現不合規格/不妥當之處? (請剔) |  |  | Type (FW, FL, FS) ^ 類別 (食水、沖廁水、消防供水) | Defects/irregularities (Please specify the extent and details of defects/irregularities, if any) 不合規格/不妥當之處(如有，則請訂明不合規格/不妥當的程度和詳情) | Details of Inspected Location (refers code below, if applicable) 已視察位置的詳情(請參見下方的編號，如適用) | Details (e.g. Brand Name/Model No., if available) 詳情 (例如品牌名稱/型號，如有的話) | Photo Taken ( Y / N ) 夾附圖片 ( 有 / 沒有 ) | Remarks 備註
Type 類別 | Contravention of WWO / WWR or Non-compliance with WA's Requirements 違反《水務設施條例》/《水務設施規例》或 不符合水務監督的要求 |  | Yes 是 | No 否 | Not Applicable 不適用
(E) Others 其他 | (1) Sanitary fittings not properly installed / provided 潔具安裝/安置不當 | P
| (2) No stopcocks at appliances & branches 用具及支喉未裝有水掣 | P
| (3) Flushing apparatus not properly installed / provided 沖廁設備安裝/安置不當 | P
| (4) Heater not properly installed 熱水器安裝不當 | P
| (5) Use of a fitting with a threaded outlet or any device facilitating the connecting of rubber hose or another type of flexible hose without WA's written permission 在未獲水務監督書面許可的情況下，使用有螺紋接駁的裝置，或任何利便連接橡膠軟管或其他種類韌性軟管的器件 | P
| (6) Booster pump directly fed from a main 增壓泵直接由總水管抽水 | P
| (7) Water using apparatus used or installed without permission 未經許可下使用或安裝用水器具 | P
| (8) No locking device for draw-off tap that is freely accessible by the general public 公眾可自由接觸的排水龍頭缺少鎖緊裝置 | D
| (9) Designated products (showers for bathing, water taps and urinal flushing valves) used in kitchens of domestic premises and bathrooms and toilets of all premises not meeting the prescribed water efficiency requirements registered under WELS 住宅處所的廚房內，以及所有處所的浴室和洗手間內，所使用的指定產品(沐浴花灑、水龍頭和小便器沖水閥)，不符合用水效益標籤計劃下規定的用水效益要求 | D
| (10) The flow controller not being a registered product under WELS or not of appropriate water efficiency grade to form a 'combined' water saving device that meets the prescribed water efficiency requirements. 節流器並非用水效益標籤計劃下的註冊產品，或並非合適的用水效益級別以形成「組合式」節水裝置，因而未能達到規定的用水效益要求 | D
| (11) Plumbing works not constructed according to the approved drawings**: Please give details 水管工程未依批准圖則建造 **: 請說明詳情 | D / NA
| (12) Absence of the licensed plumber from the final inspection of new building project after submission of WWO 46 Part IV # 在提交WWO 46第四部分之後，持牌水喉匠缺席新建樓宇項目的最終視察# | D
@ If this contravention of WWO/WWR item is found, the Licensing Authority will consider initiating the procedures to deliberate cancellation or suspension of the plumber's licence. | [6 empty] | Code for Inspected Location已視察位置的編號:
如發現違反《水務設施條例》/《水務設施規例》，發牌當局將考慮啟動相關程序，以取消或暫時吊銷持牌水喉匠的牌照。 | [6 empty] | (a) underground pipe and connection pipe 地下喉管及接駁喉 | (g) master meter position 總水錶位 |  | (m) communal riser pipe 公用豎管
Please insert ü at the appropriate box under the "Defects/irregularities found?" column. 請在「發現不合規格/不妥當之處?」欄下的適當空格內加 ü。 | [6 empty] | (b) concealed pipework above ground 地面以上的隱藏喉管 | (h) check meter position 檢測錶位 |  | (n) communal down-feed pipe 公用下給管
^ Fresh Water 食水 (FW), Flushing Water 沖廁水 (FL), Fire Service 消防供水 (FS) | [6 empty] | (c) roof tank 天台儲水箱 | (i) meter position 水錶位 |  | (o) feed tank for swimming pool 游泳池供水箱
* Please insert the code for the corresponding type of plumbing works: 請加入相應水管工程類別的編號: | [6 empty] | (d) intermediate tank 中間儲水箱 | (j) master meter room總水錶房/chamber井 |  | (p) irrigation supply points 灌溉供水點
(a) Building of Storey 樓層 >=4 | [6 empty] | (e) break pressure tank 減壓缸 | (k) meter cabinet水錶櫃/room房 (typical典型) |  | (q) cleansing supply points 清洗用水供水點
(b) Building of Storey樓層 <4 | [6 empty] | (f) break tank 斷流水箱 | (l) meter cabinet水錶櫃/room 房(non-typical, please specify非典型, 請註明) |  | (r) hydrant, hose reel, sprinkler, fountain 消防龍頭、消防喉轆、消防花灑、噴水池
(c) Village House 村屋 | [9 empty] | (s) other location其他位置 (please specify請註明)
(d) Separate Meter 安裝獨立水錶
(e) Construction Supply 地盤供水 | [6 empty] | ASN 申請書編號:
# This item is not applicable to new building projects involving just one detached village type house. 此項並不適用於只涉及一座獨立村屋類型的新建樓宇項目。
[7 empty] | WSD Inspection Staff 水務署視察人員 | Licensed Plumber 持牌水喉匠 |  | Registered Professional Engineer 註冊專業工程師
Photos should be taken on defects / irregularities須為不合規格/不妥當之處拍照
**Approved drawings include Drawing Nos. 5-11 in Appendix II of the Guide to Application for Water Supply **批准圖則包括《申請供水指引》附錄II第5-11號圖則 | [6 empty] | Signature 簽名： | Signature 簽名： |  | Signature 簽名：
[7 empty] | Name 姓名： | Name 姓名： |  | Name 姓名：
[7 empty] | Post 職位： | Plumber's Licence No. 水喉匠牌照號碼： |  | RPE No. 註冊號碼：
[7 empty] | Date 日期： | Date 日期： |  | Date 日期：