Annex I to Form A

Annex I to Form A

Checklist on Tank Cleaning, 

Water Quality Examination and

Plumbing Inspection

(This form can be used for more than one building)

A. Name of Building(s) Inspected

___________________________                                           

B. Cleaning of Water Tanks

	Name of Building(s)
	Date of last 3 inspections
	No. of water tanks cleaned
	Name of person or agent cleaning the water tanks

	
	Date 1
	Date 2
	Date 3
	
	

	
	
	
	
	
	

	
	
	
	
	
	

	
	
	
	
	
	

	
	
	
	
	
	

	
	
	
	
	
	

	
	
	
	
	
	

	
	
	
	
	
	


Please attach documentary support on the frequency of cleaning with dates.

Any notification served to the affected consumers?                   Yes / No

Any complaint arising due to cleaning? 

                       Yes / No

If yes, actions taken to handle complaints: 
Actions taken to prevent future complaints:

C.  Water Quality Examination

The purpose of the water quality examination is to check whether or not there is any deterioration in the conditions of the plumbing that cause water quality problem.  As a guideline, at least one sample for physical and chemical analysis and another one for bacteriological analysis shall be taken from a randomly selected tap supplied from each water tank of each building.  The samples shall be taken by an independent body competent of taking water samples in a manner following the Water Supplies Department standard procedure (see page 5).

(C.1) Sampling

Date of sampling:                                                         

Samples taken by:                                                       

(C.2) Testing
Date of testing:                                                           
Names of laboratories (Note 1 Table 1 in page 3) employed for testing samples:  

Testing Results

Please complete Table 1 in page 3 and attach documentary support on the testing results.
 D.
 Inspection of Plumbing Related to Water Quality

	Name of Building(s)
	No. water tanks/pumps inspected
	Communal riser or downfeed (Yes / No)
	Date of last 3 inspections

	
	tanks
	pumps
	riser
	downfeed
	Date 1
	Date 2
	Date 3

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	


Total no. of inspections in the past 12 months:                                   
Name of Licensed Plumber or Building Services Engineer* or Building Surveyor* employed for inspection:                                                  
                                        (Plumber Licence No., if applicable)
Documentary support for the inspection results shall be submitted in the format as shown on Table 2 of page 4.

Table 1 : Samples Test Results

	
	Parameters

	
	pH
	Colour
	Turbidity
	Conduct-ivity
	Iron
	E. Coli

(Note 1)
	Total Coliform

(Note 1)

	Unit
	at 250C
	HU
	NTU
	µS/cm at 250C
	mg/l
	cfu / 100ml
	cfu / 100ml

	Acceptable Criteria
	6.5 – 9. 2
	≦15
	≦3
	≦300
	≦0.3
	0
	0

	Reporting Value/Range
	1.0 – 14.0
	3
	0.1
	2
	0.01
	0
	0

	Sampling Details ( name of Building , No. of samples and location )
	Sample test results

	Name of Building(s)
	Nos.
	Location
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	



Note 1:
The E. coli and Total Coliform tests shall be performed by an accredited laboratory.  The other tests may be carried out by other laboratories.



An accredited laboratory means a laboratory accredited under the Hong Kong Laboratory Accreditation Scheme (HOKLAS) or equivalent to perform objective testing within the scope of the Scheme and meets the HOKLAS or equivalent criteria of competence.  HOKLAS publishes a Directory of Accredited Laboratories and has an updated Internet version at: http://www.itc.gov.hk/en/quality/hkas/hoklas/directory/et.htm
Table 2 : Inspection Results: (use additional page if necessary)

Date(s) of Inspection: _______________________________________________
 
	Component
	Action
	Finding ((/()
	Follow up Actions

to be Taken

	
	
	Name of Building(s)
	

	
	
	
	
	
	
	
	
	

	Water Pipe (from connection point, communal riser to communal downfeed) and Pump
	Is there any leakage?
	
	
	
	
	
	
	

	
	Is there any serious corrosion to cause discolouration?
	
	
	
	
	
	
	

	Filter if installed
	Is it installed for supply from a water tank?
	
	
	
	
	
	
	

	
	Is it maintained with replacement of filter cartridge in accordance to the instruction given by the supplier?
	
	
	
	
	
	
	

	Water Tanks
	Is the water dirty?
	
	
	
	
	
	
	

	
	Are the tanks dirty?
	
	
	
	
	
	
	

	
	Is there any cross connection between the fresh water storage tank and the flushing or fire service water tank?
	
	
	
	
	
	
	

	
	Are the metallic components  susceptible to corrosion?
	
	
	
	
	
	
	

	
	Is there any sign of corrosion?
	
	
	
	
	
	
	

	
	Are the overflow and warning pipes functioning and free from obstructions?
	
	
	
	
	
	
	

	
	Are the access manholes provided with raised necks?
	
	
	
	
	
	
	

	
	Are the access manhole covers  double-sealed and locked?
	
	
	
	
	
	
	


Inspected by:                                                     (Name and Plumber Licence No., if applicable)

Quality Water Recognition Scheme for Buildings

Sampling for Water Quality Examination


Samples of drinking water for physical, chemical and bacteriological examinations under the above scheme shall be collected, preserved and handled using the standard techniques such as those listed below:-

	Standard Technique
	Sections to be followed

	ISO 5667 Water Quality – Sampling [1]
	Part 2: Guidance on sampling techniques

	
	Part 3: Guidance on the preservation and handling of samples

	
	Part 5: Guidance on sampling of drinking water and water used for food and beverage processing

	WHO – Guidelines for drinking-water quality 2nd Edition Volume 3 [2]
	Annex 4 Sampling methods for bacteriological testing

	APHA Standard Methods for the Examination of Water and Wastewater 22nd Edition [3]
	Section 1060 Collection and Preservation of Samples


The procedures and techniques stipulated in the above standards complement each other, which should be strictly adhered to.

Notes:

[1] International Standard ISO 5667-2, 3 and 5 Water Quality – Sampling, International Organization for Standardization, Geneve, Switzerland.

[2] Guidelines for drinking-water quality 2nd Edition Volume 3, World Health Organization, Geneva, 1997

[3] Standard Methods for the Examination of Water and Wastewater, 22nd Edition, 2012, American Public Health Association, American Water Works Association and Water Environment Federation.

* 	Submission of proof of relevant qualifications is required.








Page 1 of 5

Rev (July 2012)

10
Page 2 of 5

Rev (July 2012)


