## Part A
Parameter | Unit | Monitoring Data (04/2020-03/2021) Minimum | Monitoring Data (04/2020-03/2021) Maximum | Monitoring Data (04/2020-03/2021) Average | HKDWS | Compliance
E. coli | cfu per 100 mL | 0 | 0 | 0 | 0 | yes
Total Coliforms | cfu per 100 mL | 0 | 0 | 0 | - | -
Cryptosporidium | no. of oocyst per 1,000 L | 0 | 0 | 0 | - | -
Giardia | no. of cyst per 1,000 L | 0 | 0 | 0 | - | -

## Part B
Parameter | Unit | Monitoring Data (04/2020-03/2021) Minimum | Monitoring Data (04/2020-03/2021) Maximum | Monitoring Data (04/2020-03/2021) Average | HKDWS | Compliance
Acrylamide | µg/L | < 0.4 | < 0.4 | < 0.4 | ≤ 0.5 | yes
Alachlor | µg/L | < 5.0 | < 5.0 | < 5.0 | ≤ 20 | yes
Aldicarb | µg/L | < 2.5 | < 2.5 | < 2.5 | ≤ 10 | yes
Aldrin and Dieldrin | µg/L | < 0.008 | < 0.008 | < 0.008 | ≤ 0.03 | yes
Antimony | mg/L | < 0.001 | < 0.001 | < 0.001 | ≤ 0.02 | yes
Arsenic | mg/L | < 0.001 | < 0.001 | < 0.001 | ≤ 0.01 | yes
Atrazine and its chloro-s-triazine metabolites | µg/L | < 25 | < 25 | < 25 | ≤ 100 | yes
Barium | mg/L | 0.0018 | 0.024 | 0.014 | ≤ 0.7 | yes
Benzene | µg/L | < 2.5 | < 2.5 | < 2.5 | ≤ 10 | yes
Benzo(a)pyrene | µg/L | < 0.0020 | < 0.0020 | < 0.0020 | ≤ 0.7 | yes
Boron | mg/L | < 0.02 | 0.067 | 0.033 | ≤ 2.4 | yes
Bromate | µg/L | < 1.0 | 1.3 | < 1.0 | ≤ 10 | yes
Bromodichloromethane | µg/L | < 15 | 17 | < 15 | ≤ 60 | yes
Bromoform | µg/L | < 25 | < 25 | < 25 | ≤ 100 | yes
Cadmium | mg/L | < 0.001 | < 0.001 | < 0.001 | ≤ 0.003 | yes
Carbofuran | µg/L | < 1.2 | < 1.2 | < 1.2 | ≤ 7 | yes
Carbon tetrachloride | µg/L | < 0.50 | < 0.50 | < 0.50 | ≤ 4 | yes
Chlorate | µg/L | < 10 | 130 | 24 | ≤ 700 | yes
Chlordane | µg/L | < 0.050 | < 0.050 | < 0.050 | ≤ 0.2 | yes
Chlorine | mg/L | < 0.1 | 1.7 | 0.8 | ≤ 5 | yes
Chlorite | µg/L | < 10 | < 10 | < 10 | ≤ 700 | yes
Chloroform | µg/L | < 50 | < 50 | < 50 | ≤ 300 | yes
Chlorotoluron | µg/L | < 2.5 | < 2.5 | < 2.5 | ≤ 30 | yes
Chlorpyrifos | µg/L | < 7.5 | < 7.5 | < 7.5 | ≤ 30 | yes
Chromium | mg/L | < 0.001 | 0.0041 | < 0.001 | ≤ 0.05 | yes
Copper | mg/L | < 0.003 | 0.05 | < 0.003 | ≤ 2 | yes
Cyanazine | µg/L | < 0.15 | < 0.15 | < 0.15 | ≤ 0.6 | yes
2,4-D (or 2,4-dichlorophenoxyacetic acid) | µg/L | < 7.5 | < 7.5 | < 7.5 | ≤ 30 | yes
2,4-DB ( or 4-(2,4-dichlorophenoxy)butyric acid) | µg/L | < 22 | < 22 | < 22 | ≤ 90 | yes
DDT and metabolites | µg/L | < 0.50 | < 0.50 | < 0.50 | ≤ 1 | yes
Di(2-ethylhexyl)phthalate | µg/L | < 2 | < 2 | < 2 | ≤ 8 | yes
Dibromoacetonitrile | µg/L | < 0.5 | 0.97 | < 0.5 | ≤ 70 | yes
Dibromochloromethane | µg/L | < 25 | < 25 | < 25 | ≤ 100 | yes
1,2-Dibromo-3-chloropropane | µg/L | < 0.25 | < 0.25 | < 0.25 | ≤ 1 | yes
1,2-Dibromoethane | µg/L | < 0.10 | < 0.10 | < 0.10 | ≤ 0.4 | yes
Dichloroacetate | µg/L | < 2 | 24 | 6.8 | ≤ 50 | yes
Dichloroacetonitrile | µg/L | < 2.5 | 3 | < 2.5 | ≤ 20 | yes
1,2-Dichlorobenzene | µg/L | < 250 | < 250 | < 250 | ≤ 1000 | yes
1,4-Dichlorobenzene | µg/L | < 75 | < 75 | < 75 | ≤ 300 | yes
1,2-Dichloroethane | µg/L | < 7.5 | < 7.5 | < 7.5 | ≤ 30 | yes
1,2-Dichloroethene | µg/L | < 12 | < 12 | < 12 | ≤ 50 | yes
Dichloromethane | µg/L | < 5.0 | < 5.0 | < 5.0 | ≤ 20 | yes
1,2-Dichloropropane | µg/L | < 5.0 | < 5.0 | < 5.0 | ≤ 40 | yes
1,3-Dichloropropene | µg/L | < 5.0 | < 5.0 | < 5.0 | ≤ 20 | yes
Dichlorprop (or 2,4-DP) | µg/L | < 25 | < 25 | < 25 | ≤ 100 | yes
Dimethoate | µg/L | < 1.5 | < 1.5 | < 1.5 | ≤ 6 | yes
1,4-Dioxane | µg/L | < 1.5 | 1.8 | < 1.5 | ≤ 50 | yes
Edetic acid (EDTA) | µg/L | < 30 | < 30 | < 30 | ≤ 600 | yes
Endrin | µg/L | < 0.15 | < 0.15 | < 0.15 | ≤ 0.6 | yes
Epichlorohydrin | µg/L | < 0.1 | < 0.1 | < 0.1 | ≤ 0.4 | yes
Ethylbenzene | µg/L | < 75 | < 75 | < 75 | ≤ 300 | yes
Fenoprop (or 2,4,5-TP) | µg/L | < 2.2 | < 2.2 | < 2.2 | ≤ 9 | yes
Fluoride | mg/L | < 0.1 | 0.7 | 0.49 | ≤ 1.5 | yes
Hexachlorobutadiene | µg/L | < 0.15 | < 0.15 | < 0.15 | ≤ 0.6 | yes
Hydroxyatrazine | µg/L | < 50 | < 50 | < 50 | ≤ 200 | yes
Isoproturon | µg/L | < 2.0 | < 2.0 | < 2.0 | ≤ 9 | yes
Lead | mg/L | < 0.001 | < 0.001 | < 0.001 | ≤ 0.01 | yes
Lindane | µg/L | < 0.50 | < 0.50 | < 0.50 | ≤ 2 | yes
MCPA (or (2-methyl-4-chlorophenoxy)acetic acid) | µg/L | < 2.0 | < 2.0 | < 2.0 | ≤ 2 | yes
Mecoprop (or MCPP) | µg/L | < 2.5 | < 2.5 | < 2.5 | ≤ 10 | yes
Mercury | mg/L | < 0.00005 | < 0.00005 | < 0.00005 | ≤ 0.006 | yes
Methoxychlor | µg/L | < 5.0 | < 5.0 | < 5.0 | ≤ 20 | yes
Metolachlor | µg/L | < 2.5 | < 2.5 | < 2.5 | ≤ 10 | yes
Microcystin-LR (total) | µg/L | < 0.5 | < 0.5 | < 0.5 | ≤ 1 | yes
Molinate | µg/L | < 1.5 | < 1.5 | < 1.5 | ≤ 6 | yes
Monochloramine | mg/L | < 1.0 | < 1.0 | < 1.0 | ≤ 3 | yes
Monochloroacetate | µg/L | < 2 | < 2 | < 2 | ≤ 20 | yes
Nickel | mg/L | < 0.001 | 0.0039 | 0.0011 | ≤ 0.07 | yes
Nitrate (as NO3- ) | mg/L | < 2.5 | 12 | 4.2 | ≤ 50 | yes
Nitrilotriacetic acid | µg/L | < 30 | < 30 | < 30 | ≤ 200 | yes
Nitrite (as NO2- ) | mg/L | < 0.004 | 0.007 | < 0.004 | ≤ 3 | yes
N-Nitrosodimethylamine | µg/L | < 0.025 | < 0.025 | < 0.025 | ≤ 0.1 | yes
Pendimethalin | µg/L | < 5.0 | < 5.0 | < 5.0 | ≤ 20 | yes
Pentachlorophenol | µg/L | < 2.2 | < 2.2 | < 2.2 | ≤ 9 | yes
Selenium | mg/L | < 0.003 | < 0.003 | < 0.003 | ≤ 0.04 | yes
Simazine | µg/L | < 0.50 | < 0.50 | < 0.50 | ≤ 2 | yes
Sodium dichloroisocyanurate (as cyanuric acid) | mg/L | < 10 | < 10 | < 10 | ≤ 40 | yes
Styrene | µg/L | < 5.0 | < 5.0 | < 5.0 | ≤ 20 | yes
2,4,5-T (or 2,4,5-trichlorophenoxy acetic acid) | µg/L | < 2.2 | < 2.2 | < 2.2 | ≤ 9 | yes
Terbuthylazine | µg/L | < 1.8 | < 1.8 | < 1.8 | ≤ 7 | yes
Tetrachloroethene | µg/L | < 10 | < 10 | < 10 | ≤ 40 | yes
Toluene | µg/L | < 175 | < 175 | < 175 | ≤ 700 | yes
Trichloroacetate | µg/L | < 2 | 12 | 4.5 | ≤ 200 | yes
Trichloroethene | µg/L | < 18 | < 18 | < 18 | ≤ 20 | yes
2,4,6-Trichlorophenol | µg/L | < 50 | < 50 | < 50 | ≤ 200 | yes
Trifluralin | µg/L | < 5.0 | < 5.0 | < 5.0 | ≤ 20 | yes
Uranium | mg/L | < 0.0002 | 0.001 | < 0.0002 | ≤ 0.03 | yes
Vinyl chloride | µg/L | < 0.20 | < 0.20 | < 0.20 | ≤ 0.3 | yes
Xylenes | µg/L | < 125 | < 125 | < 125 | ≤ 500 | yes

## Part C
Parameter | Unit | Monitoring Data (04/2020-03/2021) Minimum | Monitoring Data (04/2020-03/2021) Maximum | Monitoring Data (04/2020-03/2021) Average | HKDWS Screening Level | Below Screening Level
Gross alpha activity | Bq/L | < 0.1 | < 0.1 | < 0.1 | ≤ 0.5 | yes
Gross beta activity | Bq/L | < 0.2 | < 0.2 | < 0.2 | ≤ 1.0 | yes

## Part D
Parameter | Unit | Monitoring Data (04/2020-03/2021) Minimum | Monitoring Data (04/2020-03/2021) Maximum | Monitoring Data (04/2020-03/2021) Average
pH at 25 ℃ | pH | 7 | 9.6 | 8.4
Colour | Hazen unit | < 5 | < 5 | < 5
Turbidity | NTU | < 0.1 | 6.2 | 0.2
Conductivity at 25 ℃ | µS/cm | 62 | 229 | 159
Temperature | ℃ | 13 | 32.9 | 24.9
Total alkalinity (as CaCO3) | mg/L | 7 | 78 | 28
Total hardness (as CaCO3) | mg/L | < 5 | 69 | 40
Calcium | mg/L | 1.2 | 22 | 13
Magnesium | mg/L | 0.39 | 2.3 | 1.6
Chloride | mg/L | < 5 | 18 | 11
Sulphate | mg/L | 5 | 26 | 15
Ortho-phosphates (as PO4) | mg/L | < 0.01 | 0.04 | < 0.01
Iron | mg/L | < 0.01 | 0.27 | < 0.01
Aluminium | mg/L | < 0.01 | 0.19 | 0.03
Silica (as SiO2) | mg/L | 1.1 | 16 | 9.7
Manganese | mg/L | < 0.01 | 0.03 | < 0.01